## W_SUB_INDEX
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  | SUBMITTAL DATA INDEX
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  | Low Temp Scroll
|  |  | Duluth, GA 30096 |  |  | W - Series Models WBO / WFO
|  |  | (P) 800-288-9488 / (F) 256-259-7478 |  |  | Next Generation
|  |  | http://witt.htpgusa.com |  |  | Air Cooled Condensing Unit
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
| REFRIGERANT | VOLTS / PHASE / HERTZ
|  | 208/230/1/60 |  | 208/230/3/60 | 460/3/60
| R404A | W*O200L4S-DA |  | W*O200L4S-EA | W*O200L4S-GA
|  | W*O250L4S-DA |  | W*O250L4S-EA | W*O250L4S-GA
|  | W*O300L4S-DA |  | W*O300L4S-EA | W*O300L4S-GA
|  | W*O350L4S-DA |  | W*O350L4S-EA | W*O350L4S-GA
|  | W*O400L4S-DA |  | W*O400L4S-EA | W*O400L4S-GA
|  | W*O500L4S-DA |  | W*O500L4S-EA | W*O500L4S-GA
|  | N/A |  | W*O600L4S-EA | W*O600L4S-GA
| R407A | W*O200L4S-DA |  | W*O200L4S-EA | W*O200L4S-GA
|  | W*O250L4S-DA |  | W*O250L4S-EA | W*O250L4S-GA
|  | W*O300L4S-DA |  | W*O300L4S-EA | W*O300L4S-GA
|  | W*O350L4S-DA |  | W*O350L4S-EA | W*O350L4S-GA
|  | W*O400L4S-DA |  | W*O400L4S-EA | W*O400L4S-GA
|  | W*O500L4S-DA |  | W*O500L4S-EA | W*O500L4S-GA
|  | N/A |  | W*O600L4S-EA | W*O600L4S-GA
| R407C | W*O200L4S-DA |  | W*O200L4S-EA | W*O200L4S-GA
|  | W*O250L4S-DA |  | W*O250L4S-EA | W*O250L4S-GA
|  | W*O300L4S-DA |  | W*O300L4S-EA | W*O300L4S-GA
|  | W*O350L4S-DA |  | W*O350L4S-EA | W*O350L4S-GA
|  | W*O400L4S-DA |  | W*O400L4S-EA | W*O400L4S-GA
|  | W*O500L4S-DA |  | W*O500L4S-EA | W*O500L4S-GA
|  | N/A |  | W*O600L4S-EA | W*O600L4S-GA
| R448A/R449A | W*O200L4S-DA |  | W*O200L4S-EA | W*O200L4S-GA
|  | W*O250L4S-DA |  | W*O250L4S-EA | W*O250L4S-GA
|  | W*O300L4S-DA |  | W*O300L4S-EA | W*O300L4S-GA
|  | W*O350L4S-DA |  | W*O350L4S-EA | W*O350L4S-GA
|  | W*O400L4S-DA |  | W*O400L4S-EA | W*O400L4S-GA
|  | W*O500L4S-DA |  | W*O500L4S-EA | W*O500L4S-GA
|  | N/A |  | W*O600L4S-EA | W*O600L4S-GA
NOTE | * Designates model style; "B" is non-flooded model / "F" is flooded model ("flood" = low ambient head press control valve)
W_SUB_INDEX_1115-A

## W_O200L4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 11290 | 10200 | 9180 | 8220 | 7320 | 6480 | 5700 | 4990 | 4320
| +95 Deg F |  | 10810 | 9770 | 8790 | 7870 | 7020 | 6210 | 5460 | 4770 | 4130
| +100 Deg F |  | 10320 | 9330 | 8400 | 7530 | 6710 | 5940 | 5220 | 4550 | 3930
| +105 Deg F |  | 9830 | 8890 | 8010 | 7180 | 6400 | 5670 | 4980 | 4340 | 3740
| +110 Deg F |  | 9340 | 8450 | 7610 | 6830 | 6090 | 5390 | 4740 | 4130 | 3550
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 12.2 | 61 | 1 | 6 | 20 | N/A | N/A | 26 | 35
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O200L4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 9620 | 8470 | 7440 | 6510 | 5690 | 4950 | 4280 | 3690 | 3160
| +95 Deg F |  | 9380 | 8250 | 7240 | 6340 | 5530 | 4800 | 4160 | 3570 | 3050
| +100 Deg F |  | 9130 | 8030 | 7040 | 6160 | 5370 | 4660 | 4030 | 3460 | 2950
| +105 Deg F |  | 8870 | 7800 | 6840 | 5980 | 5210 | 4520 | 3900 | 3340 | 2840
| +110 Deg F |  | 8620 | 7580 | 6640 | 5800 | 5050 | 4370 | 3770 | 3230 | 2740
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 12.1 Lb's | 15 Lb's | 3.4 Lb's | 5.4 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 12.2 | 61 | 1 | 6 | 20 | N/A | N/A | 26 | 35
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O200L4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 9090 | 7940 | 6950 | 6070 | 5300 | 4620 | 4000 | 3450 | 2930
| +95 Deg F |  | 8880 | 7750 | 6770 | 5920 | 5170 | 4490 | 3900 | 3350 | 2840
| +100 Deg F |  | 8680 | 7580 | 6620 | 5790 | 5050 | 4390 | 3810 | 3260 | 2760
| +105 Deg F |  | 8470 | 7400 | 6470 | 5650 | 4930 | 4290 | 3710 | 3170 | 2660
| +110 Deg F |  | 8270 | 7230 | 6310 | 5510 | 4800 | 4170 | 3600 | 3080 | 2570
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 12.7 Lb's | 15.7 Lb's | 3.4 Lb's | 5.4 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 12.2 | 61 | 1 | 6 | 20 | N/A | N/A | 26 | 35
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O200L4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 9960 | 8730 | 7650 | 6690 | 5850 | 5100 | 4440 | 3860 | 3360
| +95 Deg F |  | 9740 | 8540 | 7480 | 6540 | 5710 | 4970 | 4340 | 3760 | 3250
| +100 Deg F |  | 9520 | 8350 | 7310 | 6390 | 5580 | 4860 | 4230 | 3670 | 3170
| +105 Deg F |  | 9290 | 8150 | 7140 | 6250 | 5450 | 4750 | 4130 | 3570 | 3080
| +110 Deg F |  | 9080 | 7970 | 6980 | 6100 | 5330 | 4640 | 4030 | 3500 | 3010
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 11.6 Lb's | 14.3 Lb's | 3.2 Lb's | 5.1 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 12.2 | 61 | 1 | 6 | 20 | N/A | N/A | 26 | 35
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O200L4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 11290 | 10200 | 9180 | 8220 | 7320 | 6480 | 5700 | 4990 | 4320
| +95 Deg F |  | 10810 | 9770 | 8790 | 7870 | 7020 | 6210 | 5460 | 4770 | 4130
| +100 Deg F |  | 10320 | 9330 | 8400 | 7530 | 6710 | 5940 | 5220 | 4550 | 3930
| +105 Deg F |  | 9830 | 8890 | 8010 | 7180 | 6400 | 5670 | 4980 | 4340 | 3740
| +110 Deg F |  | 9340 | 8450 | 7610 | 6830 | 6090 | 5390 | 4740 | 4130 | 3550
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.3 | 55 | 1 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O200L4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 9620 | 8470 | 7440 | 6510 | 5690 | 4950 | 4280 | 3690 | 3160
| +95 Deg F |  | 9380 | 8250 | 7240 | 6340 | 5530 | 4800 | 4160 | 3570 | 3050
| +100 Deg F |  | 9130 | 8030 | 7040 | 6160 | 5370 | 4660 | 4030 | 3460 | 2950
| +105 Deg F |  | 8870 | 7800 | 6840 | 5980 | 5210 | 4520 | 3900 | 3340 | 2840
| +110 Deg F |  | 8620 | 7580 | 6640 | 5800 | 5050 | 4370 | 3770 | 3230 | 2740
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 12.1 Lb's | 15 Lb's | 3.4 Lb's | 5.4 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.3 | 55 | 1 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O200L4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 9090 | 7940 | 6950 | 6070 | 5300 | 4620 | 4000 | 3450 | 2930
| +95 Deg F |  | 8880 | 7750 | 6770 | 5920 | 5170 | 4490 | 3900 | 3350 | 2840
| +100 Deg F |  | 8680 | 7580 | 6620 | 5790 | 5050 | 4390 | 3810 | 3260 | 2760
| +105 Deg F |  | 8470 | 7400 | 6470 | 5650 | 4930 | 4290 | 3710 | 3170 | 2660
| +110 Deg F |  | 8270 | 7230 | 6310 | 5510 | 4800 | 4170 | 3600 | 3080 | 2570
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 12.7 Lb's | 15.7 Lb's | 3.4 Lb's | 5.4 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.3 | 55 | 1 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O200L4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 9960 | 8730 | 7650 | 6690 | 5850 | 5100 | 4440 | 3860 | 3360
| +95 Deg F |  | 9740 | 8540 | 7480 | 6540 | 5710 | 4970 | 4340 | 3760 | 3250
| +100 Deg F |  | 9520 | 8350 | 7310 | 6390 | 5580 | 4860 | 4230 | 3670 | 3170
| +105 Deg F |  | 9290 | 8150 | 7140 | 6250 | 5450 | 4750 | 4130 | 3570 | 3080
| +110 Deg F |  | 9080 | 7970 | 6980 | 6100 | 5330 | 4640 | 4030 | 3500 | 3010
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 11.6 Lb's | 14.3 Lb's | 3.2 Lb's | 5.1 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.3 | 55 | 1 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O200L4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 11290 | 10200 | 9180 | 8220 | 7320 | 6480 | 5700 | 4990 | 4320
| +95 Deg F |  | 10810 | 9770 | 8790 | 7870 | 7020 | 6210 | 5460 | 4770 | 4130
| +100 Deg F |  | 10320 | 9330 | 8400 | 7530 | 6710 | 5940 | 5220 | 4550 | 3930
| +105 Deg F |  | 9830 | 8890 | 8010 | 7180 | 6400 | 5670 | 4980 | 4340 | 3740
| +110 Deg F |  | 9340 | 8450 | 7610 | 6830 | 6090 | 5390 | 4740 | 4130 | 3550
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.8 | 27 | 0.8 | 3 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O200L4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 9620 | 8470 | 7440 | 6510 | 5690 | 4950 | 4280 | 3690 | 3160
| +95 Deg F |  | 9380 | 8250 | 7240 | 6340 | 5530 | 4800 | 4160 | 3570 | 3050
| +100 Deg F |  | 9130 | 8030 | 7040 | 6160 | 5370 | 4660 | 4030 | 3460 | 2950
| +105 Deg F |  | 8870 | 7800 | 6840 | 5980 | 5210 | 4520 | 3900 | 3340 | 2840
| +110 Deg F |  | 8620 | 7580 | 6640 | 5800 | 5050 | 4370 | 3770 | 3230 | 2740
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 12.1 Lb's | 15 Lb's | 3.4 Lb's | 5.4 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.8 | 27 | 0.8 | 3 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O200L4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 9090 | 7940 | 6950 | 6070 | 5300 | 4620 | 4000 | 3450 | 2930
| +95 Deg F |  | 8880 | 7750 | 6770 | 5920 | 5170 | 4490 | 3900 | 3350 | 2840
| +100 Deg F |  | 8680 | 7580 | 6620 | 5790 | 5050 | 4390 | 3810 | 3260 | 2760
| +105 Deg F |  | 8470 | 7400 | 6470 | 5650 | 4930 | 4290 | 3710 | 3170 | 2660
| +110 Deg F |  | 8270 | 7230 | 6310 | 5510 | 4800 | 4170 | 3600 | 3080 | 2570
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 12.7 Lb's | 15.7 Lb's | 3.4 Lb's | 5.4 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.8 | 27 | 0.8 | 3 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O200L4S-GA_R448A_R449
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 9960 | 8730 | 7650 | 6690 | 5850 | 5100 | 4440 | 3860 | 3360
| +95 Deg F |  | 9740 | 8540 | 7480 | 6540 | 5710 | 4970 | 4340 | 3760 | 3250
| +100 Deg F |  | 9520 | 8350 | 7310 | 6390 | 5580 | 4860 | 4230 | 3670 | 3170
| +105 Deg F |  | 9290 | 8150 | 7140 | 6250 | 5450 | 4750 | 4130 | 3570 | 3080
| +110 Deg F |  | 9080 | 7970 | 6980 | 6100 | 5330 | 4640 | 4030 | 3500 | 3010
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF06K4E |  | 2 | 2 | 11.6 Lb's | 14.3 Lb's | 3.2 Lb's | 5.1 Lb's | 3/8" | 7/8" | 71 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.8 | 27 | 0.8 | 3 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 14770 | 13290 | 11910 | 10640 | 9470 | 8390 | 7400 | 6500 | 5670
| +95 Deg F |  | 14130 | 12720 | 11410 | 10190 | 9070 | 8040 | 7090 | 6210 | 5420
| +100 Deg F |  | 13490 | 12140 | 10890 | 9730 | 8660 | 7670 | 6760 | 5920 | 5160
| +105 Deg F |  | 12830 | 11550 | 10350 | 9250 | 8230 | 7290 | 6420 | 5620 | 4890
| +110 Deg F |  | 12150 | 10940 | 9810 | 8760 | 7790 | 6900 | 6070 | 5320 | 4620
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 3/8" | 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 14.7 | 73 | 1 | 10 | 25 | N/A | N/A | 32 | 45
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 12820 | 11450 | 10170 | 8990 | 7900 | 6910 | 6000 | 5190 | 4470
| +95 Deg F |  | 12390 | 11060 | 9830 | 8690 | 7630 | 6670 | 5790 | 5000 | 4300
| +100 Deg F |  | 11940 | 10660 | 9470 | 8370 | 7350 | 6420 | 5570 | 4810 | 4130
| +105 Deg F |  | 11480 | 10260 | 9110 | 8050 | 7070 | 6170 | 5350 | 4610 | 3950
| +110 Deg F |  | 11010 | 9840 | 8730 | 7710 | 6770 | 5900 | 5120 | 4400 | 3770
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E |  | 2.5 | 2 | 15 Lb's | 23.1 Lb's | 4.2 Lb's | 8.63 Lb's | 3/8" | 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 14.7 | 73 | 1 | 10 | 25 | N/A | N/A | 32 | 45
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 12220 | 10850 | 9610 | 8490 | 7460 | 6530 | 5670 | 4890 | 4170
| +95 Deg F |  | 11810 | 10490 | 9300 | 8210 | 7210 | 6310 | 5480 | 4720 | 4010
| +100 Deg F |  | 11410 | 10130 | 8970 | 7920 | 6960 | 6090 | 5290 | 4550 | 3870
| +105 Deg F |  | 10990 | 9770 | 8650 | 7630 | 6710 | 5870 | 5090 | 4380 | 3720
| +110 Deg F |  | 10560 | 9380 | 8300 | 7320 | 6440 | 5630 | 4890 | 4200 | 3570
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E |  | 2.5 | 2 | 15.7 Lb's | 24.1 Lb's | 4.2 Lb's | 8.6 Lb's | 3/8" | 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 14.7 | 73 | 1 | 10 | 25 | N/A | N/A | 32 | 45
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 12220 | 10850 | 9610 | 8490 | 7460 | 6530 | 5670 | 4890 | 4170
| +95 Deg F |  | 11810 | 10490 | 9300 | 8210 | 7210 | 6310 | 5480 | 4720 | 4010
| +100 Deg F |  | 11410 | 10130 | 8970 | 7920 | 6960 | 6090 | 5290 | 4550 | 3870
| +105 Deg F |  | 10990 | 9770 | 8650 | 7630 | 6710 | 5870 | 5090 | 4380 | 3720
| +110 Deg F |  | 10560 | 9380 | 8300 | 7320 | 6440 | 5630 | 4890 | 4200 | 3570
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E | Saturated Suction Temperature (SST) -5 F: 2.5; Saturated Suction Temperature (SST) -10 F: 2; Saturated Suction Temperature (SST) -35 F: 3/8"; Saturated Suction Temperature (SST) -40 F: 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 14.7 | 73 | 1 | 10 | 25 | N/A | N/A | 32 | 45
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 14770 | 13290 | 11910 | 10640 | 9470 | 8390 | 7400 | 6500 | 5670
| +95 Deg F |  | 14130 | 12720 | 11410 | 10190 | 9070 | 8040 | 7090 | 6210 | 5420
| +100 Deg F |  | 13490 | 12140 | 10890 | 9730 | 8660 | 7670 | 6760 | 5920 | 5160
| +105 Deg F |  | 12830 | 11550 | 10350 | 9250 | 8230 | 7290 | 6420 | 5620 | 4890
| +110 Deg F |  | 12150 | 10940 | 9810 | 8760 | 7790 | 6900 | 6070 | 5320 | 4620
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 3/8" | 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 63 | 1 | 10 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 12820 | 11450 | 10170 | 8990 | 7900 | 6910 | 6000 | 5190 | 4470
| +95 Deg F |  | 12390 | 11060 | 9830 | 8690 | 7630 | 6670 | 5790 | 5000 | 4300
| +100 Deg F |  | 11940 | 10660 | 9470 | 8370 | 7350 | 6420 | 5570 | 4810 | 4130
| +105 Deg F |  | 11480 | 10260 | 9110 | 8050 | 7070 | 6170 | 5350 | 4610 | 3950
| +110 Deg F |  | 11010 | 9840 | 8730 | 7710 | 6770 | 5900 | 5120 | 4400 | 3770
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E |  | 2.5 | 2 | 15 Lb's | 23.1 Lb's | 4.2 Lb's | 8.63 Lb's | 3/8" | 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 63 | 1 | 10 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 12220 | 10850 | 9610 | 8490 | 7460 | 6530 | 5670 | 4890 | 4170
| +95 Deg F |  | 11810 | 10490 | 9300 | 8210 | 7210 | 6310 | 5480 | 4720 | 4010
| +100 Deg F |  | 11410 | 10130 | 8970 | 7920 | 6960 | 6090 | 5290 | 4550 | 3870
| +105 Deg F |  | 10990 | 9770 | 8650 | 7630 | 6710 | 5870 | 5090 | 4380 | 3720
| +110 Deg F |  | 10560 | 9380 | 8300 | 7320 | 6440 | 5630 | 4890 | 4200 | 3570
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E |  | 2.5 | 2 | 15.7 Lb's | 24.1 Lb's | 4.2 Lb's | 8.6 Lb's | 3/8" | 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 63 | 1 | 10 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 12220 | 10850 | 9610 | 8490 | 7460 | 6530 | 5670 | 4890 | 4170
| +95 Deg F |  | 11810 | 10490 | 9300 | 8210 | 7210 | 6310 | 5480 | 4720 | 4010
| +100 Deg F |  | 11410 | 10130 | 8970 | 7920 | 6960 | 6090 | 5290 | 4550 | 3870
| +105 Deg F |  | 10990 | 9770 | 8650 | 7630 | 6710 | 5870 | 5090 | 4380 | 3720
| +110 Deg F |  | 10560 | 9380 | 8300 | 7320 | 6440 | 5630 | 4890 | 4200 | 3570
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E |  | 2.5 | 2 | 14.3 Lb's | 22 Lb's | 4 Lb's | 8.23 Lb's | 3/8" | 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 63 | 1 | 10 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 14770 | 13290 | 11910 | 10640 | 9470 | 8390 | 7400 | 6500 | 5670
| +95 Deg F |  | 14130 | 12720 | 11410 | 10190 | 9070 | 8040 | 7090 | 6210 | 5420
| +100 Deg F |  | 13490 | 12140 | 10890 | 9730 | 8660 | 7670 | 6760 | 5920 | 5160
| +105 Deg F |  | 12830 | 11550 | 10350 | 9250 | 8230 | 7290 | 6420 | 5620 | 4890
| +110 Deg F |  | 12150 | 10940 | 9810 | 8760 | 7790 | 6900 | 6070 | 5320 | 4620
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 3/8" | 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.5 | 31 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 12820 | 11450 | 10170 | 8990 | 7900 | 6910 | 6000 | 5190 | 4470
| +95 Deg F |  | 12390 | 11060 | 9830 | 8690 | 7630 | 6670 | 5790 | 5000 | 4300
| +100 Deg F |  | 11940 | 10660 | 9470 | 8370 | 7350 | 6420 | 5570 | 4810 | 4130
| +105 Deg F |  | 11480 | 10260 | 9110 | 8050 | 7070 | 6170 | 5350 | 4610 | 3950
| +110 Deg F |  | 11010 | 9840 | 8730 | 7710 | 6770 | 5900 | 5120 | 4400 | 3770
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E |  | 2.5 | 2 | 15 Lb's | 23.1 Lb's | 4.2 Lb's | 8.63 Lb's | 3/8" | 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.5 | 31 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 12220 | 10850 | 9610 | 8490 | 7460 | 6530 | 5670 | 4890 | 4170
| +95 Deg F |  | 11810 | 10490 | 9300 | 8210 | 7210 | 6310 | 5480 | 4720 | 4010
| +100 Deg F |  | 11410 | 10130 | 8970 | 7920 | 6960 | 6090 | 5290 | 4550 | 3870
| +105 Deg F |  | 10990 | 9770 | 8650 | 7630 | 6710 | 5870 | 5090 | 4380 | 3720
| +110 Deg F |  | 10560 | 9380 | 8300 | 7320 | 6440 | 5630 | 4890 | 4200 | 3570
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E |  | 2.5 | 2 | 15.7 Lb's | 24.1 Lb's | 4.2 Lb's | 8.6 Lb's | 3/8" | 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.5 | 31 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O250L4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 12220 | 10850 | 9610 | 8490 | 7460 | 6530 | 5670 | 4890 | 4170
| +95 Deg F |  | 11810 | 10490 | 9300 | 8210 | 7210 | 6310 | 5480 | 4720 | 4010
| +100 Deg F |  | 11410 | 10130 | 8970 | 7920 | 6960 | 6090 | 5290 | 4550 | 3870
| +105 Deg F |  | 10990 | 9770 | 8650 | 7630 | 6710 | 5870 | 5090 | 4380 | 3720
| +110 Deg F |  | 10560 | 9380 | 8300 | 7320 | 6440 | 5630 | 4890 | 4200 | 3570
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF08K4E |  | 2.5 | 2 | 14.3 Lb's | 22 Lb's | 4 Lb's | 8.23 Lb's | 3/8" | 7/8" | 73 | 216 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.5 | 31 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 16190 | 14610 | 13130 | 11760 | 10500 | 9320 | 8240 | 7230 | 6290
| +95 Deg F |  | 15480 | 13980 | 12570 | 11260 | 10050 | 8930 | 7890 | 6920 | 6020
| +100 Deg F |  | 14760 | 13340 | 11990 | 10750 | 9590 | 8520 | 7530 | 6600 | 5740
| +105 Deg F |  | 14040 | 12680 | 11410 | 10220 | 9120 | 8100 | 7160 | 6280 | 5450
| +110 Deg F |  | 13300 | 12010 | 10810 | 9690 | 8650 | 7680 | 6780 | 5940 | 5160
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 16 | 88 | 1 | 10 | 25 | N/A | N/A | 32 | 45
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 14170 | 12830 | 11470 | 10140 | 8870 | 7710 | 6690 | 5840 | 5190
| +95 Deg F |  | 13700 | 12410 | 11110 | 9820 | 8590 | 7460 | 6460 | 5630 | 4990
| +100 Deg F |  | 13240 | 12000 | 10740 | 9500 | 8310 | 7220 | 6240 | 5430 | 4800
| +105 Deg F |  | 12770 | 11590 | 10380 | 9190 | 8040 | 6970 | 6030 | 5230 | 4610
| +110 Deg F |  | 12310 | 11180 | 10020 | 8870 | 7770 | 6740 | 5820 | 5040 | 4430
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 4.2 Lb's | 8.63 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 16 | 88 | 1 | 10 | 25 | N/A | N/A | 32 | 45
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 13500 | 12160 | 10840 | 9570 | 8380 | 7290 | 6320 | 5500 | 4840
| +95 Deg F |  | 13060 | 11770 | 10510 | 9280 | 8120 | 7060 | 6110 | 5310 | 4660
| +100 Deg F |  | 12650 | 11400 | 10170 | 8990 | 7870 | 6850 | 5920 | 5140 | 4500
| +105 Deg F |  | 12230 | 11030 | 9850 | 8710 | 7630 | 6630 | 5740 | 4970 | 4340
| +110 Deg F |  | 11810 | 10660 | 9530 | 8430 | 7390 | 6430 | 5560 | 4810 | 4190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 15.7 Lb's | 24.1 Lb's | 4.2 Lb's | 8.6 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 16 | 88 | 1 | 10 | 25 | N/A | N/A | 32 | 45
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 13500 | 12160 | 10840 | 9570 | 8380 | 7290 | 6320 | 5500 | 4840
| +95 Deg F |  | 13060 | 11770 | 10510 | 9280 | 8120 | 7060 | 6110 | 5310 | 4660
| +100 Deg F |  | 12650 | 11400 | 10170 | 8990 | 7870 | 6850 | 5920 | 5140 | 4500
| +105 Deg F |  | 12230 | 11030 | 9850 | 8710 | 7630 | 6630 | 5740 | 4970 | 4340
| +110 Deg F |  | 11810 | 10660 | 9530 | 8430 | 7390 | 6430 | 5560 | 4810 | 4190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 14.3 Lb's | 22 Lb's | 4 Lb's | 8.23 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 16 | 88 | 1 | 10 | 25 | N/A | N/A | 32 | 45
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 16190 | 14610 | 13130 | 11760 | 10500 | 9320 | 8240 | 7230 | 6290
| +95 Deg F |  | 15480 | 13980 | 12570 | 11260 | 10050 | 8930 | 7890 | 6920 | 6020
| +100 Deg F |  | 14760 | 13340 | 11990 | 10750 | 9590 | 8520 | 7530 | 6600 | 5740
| +105 Deg F |  | 14040 | 12680 | 11410 | 10220 | 9120 | 8100 | 7160 | 6280 | 5450
| +110 Deg F |  | 13300 | 12010 | 10810 | 9690 | 8650 | 7680 | 6780 | 5940 | 5160
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 77 | 1 | 10 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 14170 | 12830 | 11470 | 10140 | 8870 | 7710 | 6690 | 5840 | 5190
| +95 Deg F |  | 13700 | 12410 | 11110 | 9820 | 8590 | 7460 | 6460 | 5630 | 4990
| +100 Deg F |  | 13240 | 12000 | 10740 | 9500 | 8310 | 7220 | 6240 | 5430 | 4800
| +105 Deg F |  | 12770 | 11590 | 10380 | 9190 | 8040 | 6970 | 6030 | 5230 | 4610
| +110 Deg F |  | 12310 | 11180 | 10020 | 8870 | 7770 | 6740 | 5820 | 5040 | 4430
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 4.2 Lb's | 8.63 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 77 | 1 | 10 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 13500 | 12160 | 10840 | 9570 | 8380 | 7290 | 6320 | 5500 | 4840
| +95 Deg F |  | 13060 | 11770 | 10510 | 9280 | 8120 | 7060 | 6110 | 5310 | 4660
| +100 Deg F |  | 12650 | 11400 | 10170 | 8990 | 7870 | 6850 | 5920 | 5140 | 4500
| +105 Deg F |  | 12230 | 11030 | 9850 | 8710 | 7630 | 6630 | 5740 | 4970 | 4340
| +110 Deg F |  | 11810 | 10660 | 9530 | 8430 | 7390 | 6430 | 5560 | 4810 | 4190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 15.7 Lb's | 24.1 Lb's | 4.2 Lb's | 8.6 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 77 | 1 | 10 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 13500 | 12160 | 10840 | 9570 | 8380 | 7290 | 6320 | 5500 | 4840
| +95 Deg F |  | 13060 | 11770 | 10510 | 9280 | 8120 | 7060 | 6110 | 5310 | 4660
| +100 Deg F |  | 12650 | 11400 | 10170 | 8990 | 7870 | 6850 | 5920 | 5140 | 4500
| +105 Deg F |  | 12230 | 11030 | 9850 | 8710 | 7630 | 6630 | 5740 | 4970 | 4340
| +110 Deg F |  | 11810 | 10660 | 9530 | 8430 | 7390 | 6430 | 5560 | 4810 | 4190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 14.3 Lb's | 22 Lb's | 4 Lb's | 8.23 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 77 | 1 | 10 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 16190 | 14610 | 13130 | 11760 | 10500 | 9320 | 8240 | 7230 | 6290
| +95 Deg F |  | 15480 | 13980 | 12570 | 11260 | 10050 | 8930 | 7890 | 6920 | 6020
| +100 Deg F |  | 14760 | 13340 | 11990 | 10750 | 9590 | 8520 | 7530 | 6600 | 5740
| +105 Deg F |  | 14040 | 12680 | 11410 | 10220 | 9120 | 8100 | 7160 | 6280 | 5450
| +110 Deg F |  | 13300 | 12010 | 10810 | 9690 | 8650 | 7680 | 6780 | 5940 | 5160
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.5 | 39 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 14170 | 12830 | 11470 | 10140 | 8870 | 7710 | 6690 | 5840 | 5190
| +95 Deg F |  | 13700 | 12410 | 11110 | 9820 | 8590 | 7460 | 6460 | 5630 | 4990
| +100 Deg F |  | 13240 | 12000 | 10740 | 9500 | 8310 | 7220 | 6240 | 5430 | 4800
| +105 Deg F |  | 12770 | 11590 | 10380 | 9190 | 8040 | 6970 | 6030 | 5230 | 4610
| +110 Deg F |  | 12310 | 11180 | 10020 | 8870 | 7770 | 6740 | 5820 | 5040 | 4430
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 4.2 Lb's | 8.63 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.5 | 39 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 13500 | 12160 | 10840 | 9570 | 8380 | 7290 | 6320 | 5500 | 4840
| +95 Deg F |  | 13060 | 11770 | 10510 | 9280 | 8120 | 7060 | 6110 | 5310 | 4660
| +100 Deg F |  | 12650 | 11400 | 10170 | 8990 | 7870 | 6850 | 5920 | 5140 | 4500
| +105 Deg F |  | 12230 | 11030 | 9850 | 8710 | 7630 | 6630 | 5740 | 4970 | 4340
| +110 Deg F |  | 11810 | 10660 | 9530 | 8430 | 7390 | 6430 | 5560 | 4810 | 4190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 15.7 Lb's | 24.1 Lb's | 4.2 Lb's | 8.6 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.5 | 39 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O300L4S-GA_R448A_R449A (hidden)
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 13500 | 12160 | 10840 | 9570 | 8380 | 7290 | 6320 | 5500 | 4840
| +95 Deg F |  | 13060 | 11770 | 10510 | 9280 | 8120 | 7060 | 6110 | 5310 | 4660
| +100 Deg F |  | 12650 | 11400 | 10170 | 8990 | 7870 | 6850 | 5920 | 5140 | 4500
| +105 Deg F |  | 12230 | 11030 | 9850 | 8710 | 7630 | 6630 | 5740 | 4970 | 4340
| +110 Deg F |  | 11810 | 10660 | 9530 | 8430 | 7390 | 6430 | 5560 | 4810 | 4190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF09K4E |  | 3 | 2 | 14.3 Lb's | 22 Lb's | 4 Lb's | 8.23 Lb's | 3/8" | 7/8" | 73 | 220 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.5 | 39 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 19400 | 17560 | 15830 | 14190 | 12670 | 11260 | 9950 | 8750 | 7630
| +95 Deg F |  | 18530 | 16780 | 15130 | 13580 | 12120 | 10780 | 9530 | 8380 | 7310
| +100 Deg F |  | 17650 | 15980 | 14410 | 12940 | 11560 | 10280 | 9090 | 8000 | 6980
| +105 Deg F |  | 16740 | 15160 | 13670 | 12290 | 10980 | 9760 | 8640 | 7600 | 6640
| +110 Deg F |  | 15820 | 14320 | 12920 | 11610 | 10380 | 9230 | 8170 | 7190 | 6280
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 18.6 | 109 | 1 | 10 | 30 | N/A | N/A | 38 | 50
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 17510 | 15880 | 14210 | 12560 | 10990 | 9530 | 8260 | 7200 | 6410
| +95 Deg F |  | 16920 | 15360 | 13750 | 12160 | 10630 | 9220 | 7980 | 6950 | 6170
| +100 Deg F |  | 16330 | 14830 | 13290 | 11750 | 10280 | 8920 | 7710 | 6700 | 5930
| +105 Deg F |  | 15730 | 14300 | 12820 | 11350 | 9930 | 8610 | 7440 | 6460 | 5710
| +110 Deg F |  | 15130 | 13760 | 12350 | 10940 | 9580 | 8310 | 7170 | 6220 | 5480
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 13.6 Lb's | 20.9 Lb's | 4.2 Lb's | 8.63 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 18.6 | 109 | 1 | 10 | 30 | N/A | N/A | 38 | 50
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 16600 | 15020 | 13420 | 11840 | 10340 | 8950 | 7750 | 6760 | 6040
| +95 Deg F |  | 16050 | 14540 | 12990 | 11470 | 10010 | 8670 | 7490 | 6530 | 5820
| +100 Deg F |  | 15530 | 14070 | 12580 | 11100 | 9690 | 8390 | 7250 | 6310 | 5600
| +105 Deg F |  | 15000 | 13600 | 12160 | 10740 | 9370 | 8110 | 7000 | 6090 | 5400
| +110 Deg F |  | 14480 | 13120 | 11740 | 10370 | 9050 | 7840 | 6750 | 5860 | 5190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 15.7 Lb's | 24.1 Lb's | 4.2 Lb's | 8.6 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 18.6 | 109 | 1 | 10 | 30 | N/A | N/A | 38 | 50
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 16600 | 15020 | 13420 | 11840 | 10340 | 8950 | 7750 | 6760 | 6040
| +95 Deg F |  | 16050 | 14540 | 12990 | 11470 | 10010 | 8670 | 7490 | 6530 | 5820
| +100 Deg F |  | 15530 | 14070 | 12580 | 11100 | 9690 | 8390 | 7250 | 6310 | 5600
| +105 Deg F |  | 15000 | 13600 | 12160 | 10740 | 9370 | 8110 | 7000 | 6090 | 5400
| +110 Deg F |  | 14480 | 13120 | 11740 | 10370 | 9050 | 7840 | 6750 | 5860 | 5190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 14.3 Lb's | 22 Lb's | 4 Lb's | 8.23 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 18.6 | 109 | 1 | 10 | 30 | N/A | N/A | 38 | 50
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 19400 | 17560 | 15830 | 14190 | 12670 | 11260 | 9950 | 8750 | 7630
| +95 Deg F |  | 18530 | 16780 | 15130 | 13580 | 12120 | 10780 | 9530 | 8380 | 7310
| +100 Deg F |  | 17650 | 15980 | 14410 | 12940 | 11560 | 10280 | 9090 | 8000 | 6980
| +105 Deg F |  | 16740 | 15160 | 13670 | 12290 | 10980 | 9760 | 8640 | 7600 | 6640
| +110 Deg F |  | 15820 | 14320 | 12920 | 11610 | 10380 | 9230 | 8170 | 7190 | 6280
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 10.9 | 88 | 1 | 10 | 25 | N/A | N/A | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 17510 | 15880 | 14210 | 12560 | 10990 | 9530 | 8260 | 7200 | 6410
| +95 Deg F |  | 16920 | 15360 | 13750 | 12160 | 10630 | 9220 | 7980 | 6950 | 6170
| +100 Deg F |  | 16330 | 14830 | 13290 | 11750 | 10280 | 8920 | 7710 | 6700 | 5930
| +105 Deg F |  | 15730 | 14300 | 12820 | 11350 | 9930 | 8610 | 7440 | 6460 | 5710
| +110 Deg F |  | 15130 | 13760 | 12350 | 10940 | 9580 | 8310 | 7170 | 6220 | 5480
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 13.6 Lb's | 20.9 Lb's | 4.2 Lb's | 8.63 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 10.9 | 88 | 1 | 10 | 25 | N/A | N/A | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 16600 | 15020 | 13420 | 11840 | 10340 | 8950 | 7750 | 6760 | 6040
| +95 Deg F |  | 16050 | 14540 | 12990 | 11470 | 10010 | 8670 | 7490 | 6530 | 5820
| +100 Deg F |  | 15530 | 14070 | 12580 | 11100 | 9690 | 8390 | 7250 | 6310 | 5600
| +105 Deg F |  | 15000 | 13600 | 12160 | 10740 | 9370 | 8110 | 7000 | 6090 | 5400
| +110 Deg F |  | 14480 | 13120 | 11740 | 10370 | 9050 | 7840 | 6750 | 5860 | 5190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 15.7 Lb's | 24.1 Lb's | 4.2 Lb's | 8.6 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 10.9 | 88 | 1 | 10 | 25 | N/A | N/A | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 16600 | 15020 | 13420 | 11840 | 10340 | 8950 | 7750 | 6760 | 6040
| +95 Deg F |  | 16050 | 14540 | 12990 | 11470 | 10010 | 8670 | 7490 | 6530 | 5820
| +100 Deg F |  | 15530 | 14070 | 12580 | 11100 | 9690 | 8390 | 7250 | 6310 | 5600
| +105 Deg F |  | 15000 | 13600 | 12160 | 10740 | 9370 | 8110 | 7000 | 6090 | 5400
| +110 Deg F |  | 14480 | 13120 | 11740 | 10370 | 9050 | 7840 | 6750 | 5860 | 5190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 14.3 Lb's | 22 Lb's | 4 Lb's | 8.23 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 10.9 | 88 | 1 | 10 | 25 | N/A | N/A | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 19400 | 17560 | 15830 | 14190 | 12670 | 11260 | 9950 | 8750 | 7630
| +95 Deg F |  | 18530 | 16780 | 15130 | 13580 | 12120 | 10780 | 9530 | 8380 | 7310
| +100 Deg F |  | 17650 | 15980 | 14410 | 12940 | 11560 | 10280 | 9090 | 8000 | 6980
| +105 Deg F |  | 16740 | 15160 | 13670 | 12290 | 10980 | 9760 | 8640 | 7600 | 6640
| +110 Deg F |  | 15820 | 14320 | 12920 | 11610 | 10380 | 9230 | 8170 | 7190 | 6280
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 5.8 | 44 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 17510 | 15880 | 14210 | 12560 | 10990 | 9530 | 8260 | 7200 | 6410
| +95 Deg F |  | 16920 | 15360 | 13750 | 12160 | 10630 | 9220 | 7980 | 6950 | 6170
| +100 Deg F |  | 16330 | 14830 | 13290 | 11750 | 10280 | 8920 | 7710 | 6700 | 5930
| +105 Deg F |  | 15730 | 14300 | 12820 | 11350 | 9930 | 8610 | 7440 | 6460 | 5710
| +110 Deg F |  | 15130 | 13760 | 12350 | 10940 | 9580 | 8310 | 7170 | 6220 | 5480
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 13.6 Lb's | 20.9 Lb's | 4.2 Lb's | 8.63 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 5.8 | 44 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 16600 | 15020 | 13420 | 11840 | 10340 | 8950 | 7750 | 6760 | 6040
| +95 Deg F |  | 16050 | 14540 | 12990 | 11470 | 10010 | 8670 | 7490 | 6530 | 5820
| +100 Deg F |  | 15530 | 14070 | 12580 | 11100 | 9690 | 8390 | 7250 | 6310 | 5600
| +105 Deg F |  | 15000 | 13600 | 12160 | 10740 | 9370 | 8110 | 7000 | 6090 | 5400
| +110 Deg F |  | 14480 | 13120 | 11740 | 10370 | 9050 | 7840 | 6750 | 5860 | 5190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 15.7 Lb's | 24.1 Lb's | 4.2 Lb's | 8.6 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 5.8 | 44 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O350L4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 16600 | 15020 | 13420 | 11840 | 10340 | 8950 | 7750 | 6760 | 6040
| +95 Deg F |  | 16050 | 14540 | 12990 | 11470 | 10010 | 8670 | 7490 | 6530 | 5820
| +100 Deg F |  | 15530 | 14070 | 12580 | 11100 | 9690 | 8390 | 7250 | 6310 | 5600
| +105 Deg F |  | 15000 | 13600 | 12160 | 10740 | 9370 | 8110 | 7000 | 6090 | 5400
| +110 Deg F |  | 14480 | 13120 | 11740 | 10370 | 9050 | 7840 | 6750 | 5860 | 5190
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF11K4E |  | 3.5 | 2 | 14.3 Lb's | 22 Lb's | 4 Lb's | 8.23 Lb's | 3/8" | 7/8" | 73 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 5.8 | 44 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 23970 | 21490 | 19190 | 17060 | 15080 | 13260 | 11590 | 10090 | 8720
| +95 Deg F |  | 22930 | 20550 | 18340 | 16300 | 14390 | 12640 | 11040 | 9580 | 8270
| +100 Deg F |  | 21860 | 19590 | 17480 | 15520 | 13700 | 12020 | 10480 | 9090 | 7830
| +105 Deg F |  | 20770 | 18610 | 16600 | 14730 | 13010 | 11410 | 9940 | 8610 | 7400
| +110 Deg F |  | 19670 | 17630 | 15720 | 13950 | 12310 | 10800 | 9410 | 8150 | 7000
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11.1 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 22.4 | 129 | 3.1 | 12 | 30 | N/A | N/A | 44 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 20980 | 18640 | 16440 | 14390 | 12520 | 10860 | 9440 | 8300 | 7450
| +95 Deg F |  | 20300 | 18000 | 15830 | 13830 | 12020 | 10420 | 9070 | 7990 | 7210
| +100 Deg F |  | 19610 | 17340 | 15220 | 13270 | 11510 | 9980 | 8690 | 7680 | 6960
| +105 Deg F |  | 18890 | 16670 | 14600 | 12700 | 11000 | 9520 | 8300 | 7350 | 6700
| +110 Deg F |  | 18150 | 15970 | 13950 | 12110 | 10470 | 9060 | 7900 | 7010 | 6430
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 30.9 Lb's | 41.8 Lb's | 8.6 Lb's | 12.2 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 22.4 | 129 | 3.1 | 12 | 30 | N/A | N/A | 44 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 19620 | 17420 | 15330 | 13390 | 11610 | 10040 | 8700 | 7650 | 6890
| +95 Deg F |  | 19000 | 16830 | 14770 | 12870 | 11150 | 9640 | 8370 | 7370 | 6680
| +100 Deg F |  | 18390 | 16240 | 14230 | 12370 | 10700 | 9240 | 8030 | 7090 | 6460
| +105 Deg F |  | 17750 | 15650 | 13680 | 11860 | 10240 | 8830 | 7680 | 6800 | 6230
| +110 Deg F |  | 17100 | 15030 | 13100 | 11340 | 9780 | 8430 | 7340 | 6510 | 6000
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 32.3 Lb's | 43.7 Lb's | 8.6 Lb's | 12.1 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 22.4 | 129 | 3.1 | 12 | 30 | N/A | N/A | 44 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 19620 | 17420 | 15330 | 13390 | 11610 | 10040 | 8700 | 7650 | 6890
| +95 Deg F |  | 19000 | 16830 | 14770 | 12870 | 11150 | 9640 | 8370 | 7370 | 6680
| +100 Deg F |  | 18390 | 16240 | 14230 | 12370 | 10700 | 9240 | 8030 | 7090 | 6460
| +105 Deg F |  | 17750 | 15650 | 13680 | 11860 | 10240 | 8830 | 7680 | 6800 | 6230
| +110 Deg F |  | 18810 | 16640 | 14690 | 12940 | 11380 | 10030 | 8880 | 7900 | 7140
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 29.4 Lb's | 39.8 Lb's | 8.2 Lb's | 11.6 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 22.4 | 129 | 3.1 | 12 | 30 | N/A | N/A | 44 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 23970 | 21490 | 19190 | 17060 | 15080 | 13260 | 11590 | 10090 | 8720
| +95 Deg F |  | 22930 | 20550 | 18340 | 16300 | 14390 | 12640 | 11040 | 9580 | 8270
| +100 Deg F |  | 21860 | 19590 | 17480 | 15520 | 13700 | 12020 | 10480 | 9090 | 7830
| +105 Deg F |  | 20770 | 18610 | 16600 | 14730 | 13010 | 11410 | 9940 | 8610 | 7400
| +110 Deg F |  | 19670 | 17630 | 15720 | 13950 | 12310 | 10800 | 9410 | 8150 | 7000
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11.1 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 11.9 | 99 | 3.1 | 12 | 25 | N/A | N/A | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 20980 | 18640 | 16440 | 14390 | 12520 | 10860 | 9440 | 8300 | 7450
| +95 Deg F |  | 20300 | 18000 | 15830 | 13830 | 12020 | 10420 | 9070 | 7990 | 7210
| +100 Deg F |  | 19610 | 17340 | 15220 | 13270 | 11510 | 9980 | 8690 | 7680 | 6960
| +105 Deg F |  | 18890 | 16670 | 14600 | 12700 | 11000 | 9520 | 8300 | 7350 | 6700
| +110 Deg F |  | 18150 | 15970 | 13950 | 12110 | 10470 | 9060 | 7900 | 7010 | 6430
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 30.9 Lb's | 41.8 Lb's | 8.6 Lb's | 12.2 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 11.9 | 99 | 3.1 | 12 | 25 | N/A | N/A | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 19620 | 17420 | 15330 | 13390 | 11610 | 10040 | 8700 | 7650 | 6890
| +95 Deg F |  | 19000 | 16830 | 14770 | 12870 | 11150 | 9640 | 8370 | 7370 | 6680
| +100 Deg F |  | 18390 | 16240 | 14230 | 12370 | 10700 | 9240 | 8030 | 7090 | 6460
| +105 Deg F |  | 17750 | 15650 | 13680 | 11860 | 10240 | 8830 | 7680 | 6800 | 6230
| +110 Deg F |  | 17100 | 15030 | 13100 | 11340 | 9780 | 8430 | 7340 | 6510 | 6000
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 32.3 Lb's | 43.7 Lb's | 8.6 Lb's | 12.1 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 11.9 | 99 | 3.1 | 12 | 25 | N/A | N/A | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 19620 | 17420 | 15330 | 13390 | 11610 | 10040 | 8700 | 7650 | 6890
| +95 Deg F |  | 19000 | 16830 | 14770 | 12870 | 11150 | 9640 | 8370 | 7370 | 6680
| +100 Deg F |  | 18390 | 16240 | 14230 | 12370 | 10700 | 9240 | 8030 | 7090 | 6460
| +105 Deg F |  | 17750 | 15650 | 13680 | 11860 | 10240 | 8830 | 7680 | 6800 | 6230
| +110 Deg F |  | 18810 | 16640 | 14690 | 12940 | 11380 | 10030 | 8880 | 7900 | 7140
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 29.4 Lb's | 39.8 Lb's | 8.2 Lb's | 11.6 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 11.9 | 99 | 3.1 | 12 | 25 | N/A | N/A | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 23970 | 21490 | 19190 | 17060 | 15080 | 13260 | 11590 | 10090 | 8720
| +95 Deg F |  | 22930 | 20550 | 18340 | 16300 | 14390 | 12640 | 11040 | 9580 | 8270
| +100 Deg F |  | 21860 | 19590 | 17480 | 15520 | 13700 | 12020 | 10480 | 9090 | 7830
| +105 Deg F |  | 20770 | 18610 | 16600 | 14730 | 13010 | 11410 | 9940 | 8610 | 7400
| +110 Deg F |  | 19670 | 17630 | 15720 | 13950 | 12310 | 10800 | 9410 | 8150 | 7000
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11.1 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.4 | 49.5 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 20980 | 18640 | 16440 | 14390 | 12520 | 10860 | 9440 | 8300 | 7450
| +95 Deg F |  | 20300 | 18000 | 15830 | 13830 | 12020 | 10420 | 9070 | 7990 | 7210
| +100 Deg F |  | 19610 | 17340 | 15220 | 13270 | 11510 | 9980 | 8690 | 7680 | 6960
| +105 Deg F |  | 18890 | 16670 | 14600 | 12700 | 11000 | 9520 | 8300 | 7350 | 6700
| +110 Deg F |  | 18150 | 15970 | 13950 | 12110 | 10470 | 9060 | 7900 | 7010 | 6430
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 30.9 Lb's | 41.8 Lb's | 8.6 Lb's | 12.2 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.4 | 49.5 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 19620 | 17420 | 15330 | 13390 | 11610 | 10040 | 8700 | 7650 | 6890
| +95 Deg F |  | 19000 | 16830 | 14770 | 12870 | 11150 | 9640 | 8370 | 7370 | 6680
| +100 Deg F |  | 18390 | 16240 | 14230 | 12370 | 10700 | 9240 | 8030 | 7090 | 6460
| +105 Deg F |  | 17750 | 15650 | 13680 | 11860 | 10240 | 8830 | 7680 | 6800 | 6230
| +110 Deg F |  | 17100 | 15030 | 13100 | 11340 | 9780 | 8430 | 7340 | 6510 | 6000
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 32.3 Lb's | 43.7 Lb's | 8.6 Lb's | 12.1 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.4 | 49.5 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O400L4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 19620 | 17420 | 15330 | 13390 | 11610 | 10040 | 8700 | 7650 | 6890
| +95 Deg F |  | 19000 | 16830 | 14770 | 12870 | 11150 | 9640 | 8370 | 7370 | 6680
| +100 Deg F |  | 18390 | 16240 | 14230 | 12370 | 10700 | 9240 | 8030 | 7090 | 6460
| +105 Deg F |  | 17750 | 15650 | 13680 | 11860 | 10240 | 8830 | 7680 | 6800 | 6230
| +110 Deg F |  | 18810 | 16640 | 14690 | 12940 | 11380 | 10030 | 8880 | 7900 | 7140
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13K4E |  | 4 | 1 | 29.4 Lb's | 39.8 Lb's | 8.2 Lb's | 11.6 Lb's | 1/2" | 1-1/8" | 73 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.4 | 49.5 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 28630 | 25820 | 23200 | 20770 | 18520 | 16450 | 14530 | 12760 | 11150
| +95 Deg F |  | 27350 | 24660 | 22160 | 19840 | 17690 | 15710 | 13880 | 12200 | 10650
| +100 Deg F |  | 26040 | 23480 | 21100 | 18890 | 16850 | 14960 | 13220 | 11620 | 10150
| +105 Deg F |  | 24710 | 22280 | 20020 | 17920 | 15990 | 14200 | 12550 | 11020 | 9620
| +110 Deg F |  | 23360 | 21060 | 18920 | 16940 | 15100 | 13410 | 11850 | 10410 | 9090
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11.1 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 24.7 | 169 | 3.1 | 12 | 30 | N/A | N/A | 46 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 25620 | 22750 | 20070 | 17620 | 15420 | 13480 | 11830 | 10490 | 9490
| +95 Deg F |  | 24790 | 21990 | 19370 | 16980 | 14830 | 12960 | 11370 | 10080 | 9130
| +100 Deg F |  | 23950 | 21200 | 18650 | 16320 | 14230 | 12410 | 10880 | 9650 | 8740
| +105 Deg F |  | 23080 | 20400 | 17910 | 15640 | 13610 | 11850 | 10370 | 9190 | 8320
| +110 Deg F |  | 22180 | 19570 | 17140 | 14930 | 12970 | 11260 | 9840 | 8710 | 7890
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 30.9 Lb's | 41.8 Lb's | 8.6 Lb's | 12.2 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 24.7 | 169 | 3.1 | 12 | 30 | N/A | N/A | 46 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 23910 | 21270 | 18760 | 16440 | 14340 | 12480 | 10910 | 9660 | 8770
| +95 Deg F |  | 23160 | 20580 | 18120 | 15850 | 13800 | 12010 | 10490 | 9290 | 8450
| +100 Deg F |  | 22430 | 19880 | 17490 | 15270 | 13270 | 11520 | 10060 | 8910 | 8110
| +105 Deg F |  | 21670 | 19180 | 16830 | 14670 | 12720 | 11020 | 9610 | 8510 | 7750
| +110 Deg F |  | 20880 | 18450 | 16150 | 14040 | 12150 | 10500 | 9140 | 8090 | 7380
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 32.3 Lb's | 43.7 Lb's | 8.6 Lb's | 12.1 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 24.7 | 169 | 3.1 | 12 | 30 | N/A | N/A | 46 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 27380 | 24340 | 21540 | 19000 | 16700 | 14640 | 12810 | 11200 | 9830
| +95 Deg F |  | 26340 | 23420 | 20720 | 18280 | 16070 | 14120 | 12380 | 10850 | 9560
| +100 Deg F |  | 25260 | 22450 | 19880 | 17550 | 15440 | 13580 | 11940 | 10510 | 9290
| +105 Deg F |  | 24140 | 21460 | 19010 | 16800 | 14810 | 13050 | 11510 | 10180 | 9040
| +110 Deg F |  | 22980 | 20440 | 18120 | 16030 | 14170 | 12520 | 11100 | 9870 | 8830
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 29.4 Lb's | 39.8 Lb's | 8.2 Lb's | 11.6 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 24.7 | 169 | 3.1 | 12 | 30 | N/A | N/A | 46 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 28630 | 25820 | 23200 | 20770 | 18520 | 16450 | 14530 | 12760 | 11150
| +95 Deg F |  | 27350 | 24660 | 22160 | 19840 | 17690 | 15710 | 13880 | 12200 | 10650
| +100 Deg F |  | 26040 | 23480 | 21100 | 18890 | 16850 | 14960 | 13220 | 11620 | 10150
| +105 Deg F |  | 24710 | 22280 | 20020 | 17920 | 15990 | 14200 | 12550 | 11020 | 9620
| +110 Deg F |  | 23360 | 21060 | 18920 | 16940 | 15100 | 13410 | 11850 | 10410 | 9090
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11.1 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 17 | 123 | 3.1 | 12 | 30 | N/A | N/A | 38.5 | 50
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 25620 | 22750 | 20070 | 17620 | 15420 | 13480 | 11830 | 10490 | 9490
| +95 Deg F |  | 24790 | 21990 | 19370 | 16980 | 14830 | 12960 | 11370 | 10080 | 9130
| +100 Deg F |  | 23950 | 21200 | 18650 | 16320 | 14230 | 12410 | 10880 | 9650 | 8740
| +105 Deg F |  | 23080 | 20400 | 17910 | 15640 | 13610 | 11850 | 10370 | 9190 | 8320
| +110 Deg F |  | 22180 | 19570 | 17140 | 14930 | 12970 | 11260 | 9840 | 8710 | 7890
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 30.9 Lb's | 41.8 Lb's | 8.6 Lb's | 12.2 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 17 | 123 | 3.1 | 12 | 30 | N/A | N/A | 38.5 | 50
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 23910 | 21270 | 18760 | 16440 | 14340 | 12480 | 10910 | 9660 | 8770
| +95 Deg F |  | 23160 | 20580 | 18120 | 15850 | 13800 | 12010 | 10490 | 9290 | 8450
| +100 Deg F |  | 22430 | 19880 | 17490 | 15270 | 13270 | 11520 | 10060 | 8910 | 8110
| +105 Deg F |  | 21670 | 19180 | 16830 | 14670 | 12720 | 11020 | 9610 | 8510 | 7750
| +110 Deg F |  | 20880 | 18450 | 16150 | 14040 | 12150 | 10500 | 9140 | 8090 | 7380
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 32.3 Lb's | 43.7 Lb's | 8.6 Lb's | 12.1 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 17 | 123 | 3.1 | 12 | 30 | N/A | N/A | 38.5 | 50
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 27380 | 24340 | 21540 | 19000 | 16700 | 14640 | 12810 | 11200 | 9830
| +95 Deg F |  | 26340 | 23420 | 20720 | 18280 | 16070 | 14120 | 12380 | 10850 | 9560
| +100 Deg F |  | 25260 | 22450 | 19880 | 17550 | 15440 | 13580 | 11940 | 10510 | 9290
| +105 Deg F |  | 24140 | 21460 | 19010 | 16800 | 14810 | 13050 | 11510 | 10180 | 9040
| +110 Deg F |  | 22980 | 20440 | 18120 | 16030 | 14170 | 12520 | 11100 | 9870 | 8830
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 29.4 Lb's | 39.8 Lb's | 8.2 Lb's | 11.6 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 17 | 123 | 3.1 | 12 | 30 | N/A | N/A | 38.5 | 50
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 28630 | 25820 | 23200 | 20770 | 18520 | 16450 | 14530 | 12760 | 11150
| +95 Deg F |  | 27350 | 24660 | 22160 | 19840 | 17690 | 15710 | 13880 | 12200 | 10650
| +100 Deg F |  | 26040 | 23480 | 21100 | 18890 | 16850 | 14960 | 13220 | 11620 | 10150
| +105 Deg F |  | 24710 | 22280 | 20020 | 17920 | 15990 | 14200 | 12550 | 11020 | 9620
| +110 Deg F |  | 23360 | 21060 | 18920 | 16940 | 15100 | 13410 | 11850 | 10410 | 9090
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11.1 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8 | 62 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 25620 | 22750 | 20070 | 17620 | 15420 | 13480 | 11830 | 10490 | 9490
| +95 Deg F |  | 24790 | 21990 | 19370 | 16980 | 14830 | 12960 | 11370 | 10080 | 9130
| +100 Deg F |  | 23950 | 21200 | 18650 | 16320 | 14230 | 12410 | 10880 | 9650 | 8740
| +105 Deg F |  | 23080 | 20400 | 17910 | 15640 | 13610 | 11850 | 10370 | 9190 | 8320
| +110 Deg F |  | 22180 | 19570 | 17140 | 14930 | 12970 | 11260 | 9840 | 8710 | 7890
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 30.9 Lb's | 41.8 Lb's | 8.6 Lb's | 12.2 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8 | 62 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 23910 | 21270 | 18760 | 16440 | 14340 | 12480 | 10910 | 9660 | 8770
| +95 Deg F |  | 23160 | 20580 | 18120 | 15850 | 13800 | 12010 | 10490 | 9290 | 8450
| +100 Deg F |  | 22430 | 19880 | 17490 | 15270 | 13270 | 11520 | 10060 | 8910 | 8110
| +105 Deg F |  | 21670 | 19180 | 16830 | 14670 | 12720 | 11020 | 9610 | 8510 | 7750
| +110 Deg F |  | 20880 | 18450 | 16150 | 14040 | 12150 | 10500 | 9140 | 8090 | 7380
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 32.3 Lb's | 43.7 Lb's | 8.6 Lb's | 12.1 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8 | 62 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O500L4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 27380 | 24340 | 21540 | 19000 | 16700 | 14640 | 12810 | 11200 | 9830
| +95 Deg F |  | 26340 | 23420 | 20720 | 18280 | 16070 | 14120 | 12380 | 10850 | 9560
| +100 Deg F |  | 25260 | 22450 | 19880 | 17550 | 15440 | 13580 | 11940 | 10510 | 9290
| +105 Deg F |  | 24140 | 21460 | 19010 | 16800 | 14810 | 13050 | 11510 | 10180 | 9040
| +110 Deg F |  | 22980 | 20440 | 18120 | 16030 | 14170 | 12520 | 11100 | 9870 | 8830
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF15K4E |  | 5 | 1 | 29.4 Lb's | 39.8 Lb's | 8.2 Lb's | 11.6 Lb's | 1/2" | 1-1/8" | 74 | 330 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8 | 62 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O600L4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 32720 | 29530 | 26560 | 23790 | 21220 | 18850 | 16660 | 14630 | 12760
| +95 Deg F |  | 31310 | 28270 | 25440 | 22800 | 20350 | 18080 | 15980 | 14040 | 12240
| +100 Deg F |  | 29890 | 27000 | 24300 | 21790 | 19450 | 17290 | 15280 | 13430 | 11710
| +105 Deg F |  | 28450 | 25700 | 23140 | 20760 | 18540 | 16480 | 14580 | 12810 | 11180
| +110 Deg F |  | 26990 | 24390 | 21960 | 19700 | 17610 | 15660 | 13850 | 12180 | 10630
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF18K4E |  | 6 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11.1 Lb's | 1/2" | 1-1/8" | 76 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 19.6 | 156 | 3.1 | 12 | 30 | N/A | N/A | 40.6 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O600L4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 30490 | 27200 | 24110 | 21220 | 18600 | 16270 | 14260 | 12600 | 11320
| +95 Deg F |  | 29540 | 26330 | 23310 | 20500 | 17950 | 15690 | 13750 | 12160 | 10930
| +100 Deg F |  | 28580 | 25440 | 22500 | 19770 | 17290 | 15100 | 13230 | 11690 | 10530
| +105 Deg F |  | 27600 | 24540 | 21670 | 19020 | 16620 | 14500 | 12690 | 11210 | 10100
| +110 Deg F |  | 26600 | 23620 | 20830 | 18260 | 15930 | 13870 | 12130 | 10710 | 9650
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF18K4E |  | 6 | 1 | 30.9 Lb's | 41.8 Lb's | 8.6 Lb's | 12.2 Lb's | 1/2" | 1-1/8" | 76 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 19.6 | 156 | 3.1 | 12 | 30 | N/A | N/A | 40.6 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O600L4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 28450 | 25410 | 22510 | 19780 | 17290 | 15080 | 13190 | 11660 | 10530
| +95 Deg F |  | 27590 | 24620 | 21780 | 19120 | 16700 | 14560 | 12730 | 11260 | 10180
| +100 Deg F |  | 26770 | 23840 | 21070 | 18480 | 16120 | 14040 | 12280 | 10860 | 9840
| +105 Deg F |  | 25920 | 23050 | 20340 | 17820 | 15520 | 13510 | 11800 | 10440 | 9480
| +110 Deg F |  | 25050 | 22250 | 19600 | 17140 | 14910 | 12940 | 11300 | 10000 | 9090
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF18K4E |  | 6 | 1 | 32.3 Lb's | 43.7 Lb's | 8.6 Lb's | 12.1 Lb's | 1/2" | 1-1/8" | 76 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 19.6 | 156 | 3.1 | 12 | 30 | N/A | N/A | 40.6 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O600L4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R449A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 32560 | 29050 | 25830 | 22850 | 20140 | 17690 | 15490 | 13520 | 11790
| +95 Deg F |  | 31360 | 27990 | 24890 | 22040 | 19440 | 17110 | 15020 | 13160 | 11520
| +100 Deg F |  | 30130 | 26890 | 23930 | 21210 | 18750 | 16530 | 14560 | 12810 | 11280
| +105 Deg F |  | 28850 | 25770 | 22940 | 20380 | 18050 | 15970 | 14120 | 12480 | 11060
| +110 Deg F |  | 27540 | 24620 | 21950 | 19540 | 17370 | 15410 | 13700 | 12190 | 10880
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF18K4E |  | 6 | 1 | 29.4 Lb's | 39.8 Lb's | 8.2 Lb's | 11.6 Lb's | 1/2" | 1-1/8" | 76 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 19.6 | 156 | 3.1 | 12 | 30 | N/A | N/A | 40.6 | 60
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O600L4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 32720 | 29530 | 26560 | 23790 | 21220 | 18850 | 16660 | 14630 | 12760
| +95 Deg F |  | 31310 | 28270 | 25440 | 22800 | 20350 | 18080 | 15980 | 14040 | 12240
| +100 Deg F |  | 29890 | 27000 | 24300 | 21790 | 19450 | 17290 | 15280 | 13430 | 11710
| +105 Deg F |  | 28450 | 25700 | 23140 | 20760 | 18540 | 16480 | 14580 | 12810 | 11180
| +110 Deg F |  | 26990 | 24390 | 21960 | 19700 | 17610 | 15660 | 13850 | 12180 | 10630
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF18K4E |  | 6 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11.1 Lb's | 1/2" | 1-1/8" | 76 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8 | 75 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O600L4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 30490 | 27200 | 24110 | 21220 | 18600 | 16270 | 14260 | 12600 | 11320
| +95 Deg F |  | 29540 | 26330 | 23310 | 20500 | 17950 | 15690 | 13750 | 12160 | 10930
| +100 Deg F |  | 28580 | 25440 | 22500 | 19770 | 17290 | 15100 | 13230 | 11690 | 10530
| +105 Deg F |  | 27600 | 24540 | 21670 | 19020 | 16620 | 14500 | 12690 | 11210 | 10100
| +110 Deg F |  | 26600 | 23620 | 20830 | 18260 | 15930 | 13870 | 12130 | 10710 | 9650
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF18K4E |  | 6 | 1 | 30.9 Lb's | 41.8 Lb's | 8.6 Lb's | 12.2 Lb's | 1/2" | 1-1/8" | 76 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8 | 75 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O600L4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 28450 | 25410 | 22510 | 19780 | 17290 | 15080 | 13190 | 11660 | 10530
| +95 Deg F |  | 27590 | 24620 | 21780 | 19120 | 16700 | 14560 | 12730 | 11260 | 10180
| +100 Deg F |  | 26770 | 23840 | 21070 | 18480 | 16120 | 14040 | 12280 | 10860 | 9840
| +105 Deg F |  | 25920 | 23050 | 20340 | 17820 | 15520 | 13510 | 11800 | 10440 | 9480
| +110 Deg F |  | 25050 | 22250 | 19600 | 17140 | 14910 | 12940 | 11300 | 10000 | 9090
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF18K4E |  | 6 | 1 | 32.3 Lb's | 43.7 Lb's | 8.6 Lb's | 12.1 Lb's | 1/2" | 1-1/8" | 76 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8 | 75 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_O600L4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBO / WFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:50
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F | -35 F | -40 F
| +90 Deg F |  | 32560 | 29050 | 25830 | 22850 | 20140 | 17690 | 15490 | 13520 | 11790
| +95 Deg F |  | 31360 | 27990 | 24890 | 22040 | 19440 | 17110 | 15020 | 13160 | 11520
| +100 Deg F |  | 30130 | 26890 | 23930 | 21210 | 18750 | 16530 | 14560 | 12810 | 11280
| +105 Deg F |  | 28850 | 25770 | 22940 | 20380 | 18050 | 15970 | 14120 | 12480 | 11060
| +110 Deg F |  | 27540 | 24620 | 21950 | 19540 | 17370 | 15410 | 13700 | 12190 | 10880
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF18K4E |  | 6 | 1 | 29.4 Lb's | 39.8 Lb's | 8.2 Lb's | 11.6 Lb's | 1/2" | 1-1/8" | 76 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8 | 75 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A