## K_SUB_INDEX
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  | SUBMITTAL DATA INDEX
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  | Low Temp Hermetic
|  |  | Duluth, GA 30096 |  |  | K - Series Models KBH / KFH
|  |  | (P) 800-288-9488 / (F) 256-259-7478 |  |  | Next Generation
|  |  | http://kramer.htpgusa.com |  |  | Air Cooled Condensing Unit
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
| REFRIGERANT | VOLTS / PHASE / HERTZ
|  | 208/230/1/60 |  | 208/230/3/60 | 460/3/60
| R404A | K*H055E44-DA |  | N/A | N/A
|  | K*H080E44-DA |  | N/A | N/A
|  | K*H090E44-DA |  | N/A | N/A
|  | K*H100E44-DA |  | K*H100E44-EA | N/A
|  | K*H125E44-DA |  | K*H125E44-EA | N/A
|  | K*H150E44-DA |  | K*H150E44-EA | K*H150E44-GA
|  | K*H200E44-DA |  | K*H200E44-EA | N/A
|  | K*H250E44-DA |  | K*H250E44-EA | K*H250E44-GA
|  | K*H300E44-DA |  | K*H300E44-EA | K*H300E44-GA
|  | K*H325E44-DA |  | K*H325E44-EA | K*H325E44-GA
|  | K*H100L44-DA |  | KLH100L44-EA | KLH100L44-GA
|  | K*H150L44-DA |  | K*H150L44-EA | K*H150L44-GA
|  | K*H200L44-DA |  | K*H200L44-EA | K*H200L44-GA
|  | K*H300L44-DA |  | K*H300L44-EA | K*H300L44-GA
NOTE | * Designates model style; "B" is non-flooded model / "F" is flooded model ("flood" = low ambient head press control valve)
3720
K_SUB_INDEX_1115-A

## K_H055E44-DA-R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 3390 | 2940 | 2520 | 1700 | 1310
|  |  | +95 Deg F |  | 3210 | 2780 | 2370 | 1580 | 1200
|  |  | +100 Deg F |  | 3030 | 2620 | 2220 | 1460 | 1090
|  |  | +105 Deg F |  | 2850 | 2450 | 2070 | 1340 | 985
|  |  | +110 Deg F |  | 2660 | 2280 | 1920 | 1220 | 880
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST45C1E |  | 0.5 | 1 | 5.9 Lb's | 11 Lb's | 1.63 Lb's | 2.73 Lb's | 3/8" | 5/8" | 68 | 137 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 4.6 | 26.5 | 0.5 | 4 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H080E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 3960 | 3420 | 2930 | 2070 | 1690
|  |  | +95 Deg F |  | 3720 | 3200 | 2730 | 1900 | 1540
|  |  | +100 Deg F |  | 3490 | 2990 | 2540 | 1740 | 1400
|  |  | +105 Deg F |  | 3265 | 1833 | 2360 | 1605 | 1275
|  |  | +110 Deg F |  | 3040 | 2590 | 2180 | 1470 | 1150
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST55C1E |  | 0.5 | 1 | 5.9 Lb's | 11 Lb's | 1.63 Lb's | 2.73 Lb's | 3/8" | 5/8" | 68 | 140 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 6.1 | 33.7 | 0.5 | 4 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H090E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 5250 | 4590 | 3980 | 2870 | 2370
|  |  | +95 Deg F |  | 4970 | 4340 | 3740 | 2670 | 2200
|  |  | +100 Deg F |  | 4700 | 4090 | 3510 | 2480 | 2030
|  |  | +105 Deg F |  | 4426 | 3840 | 3290 | 2305 | 1870
|  |  | +110 Deg F |  | 4150 | 3590 | 3070 | 2130 | 1710
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST64C1E |  | 0.75 | 1 | 5.9 Lb's | 11 Lb's | 1.63 Lb's | 2.73 Lb's | 3/8" | 5/8" | 68 | 144 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 8.1 | 43 | 0.5 | 4 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H100E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 5250 | 4560 | 3920 | 2830 | 2360
|  |  | +95 Deg F |  | 4970 | 4310 | 3690 | 2640 | 2190
|  |  | +100 Deg F |  | 4690 | 4050 | 3460 | 2450 | 2020
|  |  | +105 Deg F |  | 4395 | 3785 | 3220 | 2255 | 1840
|  |  | +110 Deg F |  | 4100 | 3520 | 2980 | 2060 | 1660
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST70C1E |  | 0.75 | 1 | 5.9 Lb's | 11 Lb's | 1.63 Lb's | 2.73 Lb's | 3/8" | 5/8" | 68 | 150 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 6.9 | 46 | 0.5 | 4 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H100E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 5250 | 4560 | 3920 | 2830 | 2360
|  |  | +95 Deg F |  | 4970 | 4310 | 3690 | 2640 | 2190
|  |  | +100 Deg F |  | 4690 | 4050 | 3460 | 2450 | 2020
|  |  | +105 Deg F |  | 4395 | 3785 | 3220 | 2255 | 1840
|  |  | +110 Deg F |  | 4100 | 3520 | 2980 | 2060 | 1660
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST70C1E |  | 0.75 | 1 | 5.9 Lb's | 11 Lb's | 1.63 Lb's | 2.73 Lb's | 3/8" | 5/8" | 68 | 150 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 4.9 | 36 | 0.5 | 4 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H125E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 7640 | 6690 | 5820 | 4300 | 3680
|  |  | +95 Deg F |  | 7230 | 6320 | 5470 | 4020 | 3420
|  |  | +100 Deg F |  | 6810 | 5930 | 5120 | 3730 | 3150
|  |  | +105 Deg F |  | 6385 | 5545 | 4770 | 3435 | 2885
|  |  | +110 Deg F |  | 5960 | 5160 | 4420 | 3140 | 2620
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST97C1E |  | 1 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 1/2" | 7/8" | 72 | 175 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 9 | 51 | 1 | 4 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H125E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 7640 | 6690 | 5820 | 4300 | 3680
|  |  | +95 Deg F |  | 7230 | 6320 | 5470 | 4020 | 3420
|  |  | +100 Deg F |  | 6810 | 5930 | 5120 | 3730 | 3150
|  |  | +105 Deg F |  | 6385 | 5545 | 4770 | 3435 | 2885
|  |  | +110 Deg F |  | 5960 | 5160 | 4420 | 3140 | 2620
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST97C1E |  | 1 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 1/2" | 7/8" | 72 | 175 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 5.4 | 36 | 1 | 6 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H150E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 7530 | 6270 | 5110 | 3130 | 2340
|  |  | +95 Deg F |  | 6920 | 5720 | 4610 | 2740 | 1990
|  |  | +100 Deg F |  | 6320 | 5170 | 4120 | 2350 | 1640
|  |  | +105 Deg F |  | 5720 | 4900 | 3630 | 1960 | 1290
|  |  | +110 Deg F |  | 5120 | 4630 | 3140 | 1570 | 940
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS10K6E |  | 1.5 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 1/2" | 7/8" | 72 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 9.8 | 56 | 1 | 6 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H150E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 7530 | 6270 | 5110 | 3130 | 2340
|  |  | +95 Deg F |  | 6920 | 5720 | 4610 | 2740 | 1990
|  |  | +100 Deg F |  | 6320 | 5170 | 4120 | 2350 | 1640
|  |  | +105 Deg F |  | 5720 | 4900 | 3630 | 1960 | 1290
|  |  | +110 Deg F |  | 5120 | 4630 | 3140 | 1570 | 940
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS10K6E |  | 1.5 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 1/2" | 7/8" | 72 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 6.7 | 51 | 1 | 6 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H150E44-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 7530 | 6270 | 5110 | 3130 | 2340
|  |  | +95 Deg F |  | 6920 | 5720 | 4610 | 2740 | 1990
|  |  | +100 Deg F |  | 6320 | 5170 | 4120 | 2350 | 1640
|  |  | +105 Deg F |  | 5720 | 4900 | 3630 | 1960 | 1290
|  |  | +110 Deg F |  | 5120 | 4090 | 3140 | 1570 | 940
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS10K6E |  | 1.5 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 1/2" | 7/8" | 72 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.2 | 25 | 0.8 | 3 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H200E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 8640 | 7270 | 5970 | 3580 | 2470
|  |  | +95 Deg F |  | 7970 | 6650 | 5410 | 3130 | 2070
|  |  | +100 Deg F |  | 7300 | 6040 | 4860 | 2700 | 1690
|  |  | +105 Deg F |  | 6650 | 5455 | 4335 | 2300 | 1360
|  |  | +110 Deg F |  | 6000 | 4870 | 3810 | 1900 | 1030
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS12K6E |  | 2 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 1/2" | 7/8" | 72 | 205 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 9.8 | 56 | 1 | 6 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H200E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 8640 | 7270 | 5970 | 3580 | 2470
|  |  | +95 Deg F |  | 7970 | 6650 | 5410 | 3130 | 2070
|  |  | +100 Deg F |  | 7300 | 6040 | 4860 | 2700 | 1690
|  |  | +105 Deg F |  | 6650 | 5455 | 4335 | 2300 | 1360
|  |  | +110 Deg F |  | 6000 | 4870 | 3810 | 1900 | 1030
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS12K6E |  | 2 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 1/2" | 7/8" | 72 | 205 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 6.7 | 51 | 1 | 6 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H250E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 10980 | 9350 | 7840 | 5230 | 4150
|  |  | +95 Deg F |  | 10240 | 8690 | 7250 | 4760 | 3740
|  |  | +100 Deg F |  | 9510 | 8040 | 6670 | 4300 | 3320
|  |  | +105 Deg F |  | 8780 | 7385 | 6085 | 3845 | 2920
|  |  | +110 Deg F |  | 8050 | 6730 | 5500 | 3390 | 2520
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS14K6E |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 72 | 212 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 11.2 | 61 | 1 | 10 | 28 | N/A | N/A | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H250E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 10980 | 9350 | 7840 | 5230 | 4150
|  |  | +95 Deg F |  | 10240 | 8690 | 7250 | 4760 | 3740
|  |  | +100 Deg F |  | 9510 | 8040 | 6670 | 4300 | 3320
|  |  | +105 Deg F |  | 8780 | 7385 | 6085 | 3845 | 2920
|  |  | +110 Deg F |  | 8050 | 6730 | 5500 | 3390 | 2520
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS14K6E |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 72 | 212 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.2 | 55 | 1 | 10 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H250E44-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 10980 | 9350 | 7840 | 5230 | 4150
|  |  | +95 Deg F |  | 10240 | 8690 | 7250 | 4760 | 3740
|  |  | +100 Deg F |  | 9510 | 8040 | 6670 | 4300 | 3320
|  |  | +105 Deg F |  | 8780 | 7385 | 6085 | 3845 | 2920
|  |  | +110 Deg F |  | 8050 | 6730 | 5500 | 3390 | 2520
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS14K6E |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 72 | 212 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.2 | 28 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H300E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 13300 | 11240 | 9330 | 6120 | 4890
|  |  | +95 Deg F |  | 12310 | 10340 | 8530 | 5520 | 4370
|  |  | +100 Deg F |  | 11330 | 9470 | 7760 | 4940 | 3890
|  |  | +105 Deg F |  | 10395 | 8635 | 7025 | 4405 | 3445
|  |  | +110 Deg F |  | 9460 | 7800 | 6290 | 3870 | 3000
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS18K6E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 73 | 228 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 14.4 | 82 | 1 | 10 | 28 | N/A | N/A | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H300E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 13300 | 11240 | 9330 | 6120 | 4890
|  |  | +95 Deg F |  | 12310 | 10340 | 8530 | 5520 | 4370
|  |  | +100 Deg F |  | 11330 | 9470 | 7760 | 4940 | 3890
|  |  | +105 Deg F |  | 10395 | 8635 | 7025 | 4405 | 3445
|  |  | +110 Deg F |  | 9460 | 7800 | 6290 | 3870 | 3000
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS18K6E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 73 | 228 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 9.4 | 65.5 | 1 | 10 | 20 | N/A | N/A | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H300E44-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 13300 | 11240 | 9330 | 6120 | 4890
|  |  | +95 Deg F |  | 12310 | 10340 | 8530 | 5520 | 4370
|  |  | +100 Deg F |  | 11330 | 9470 | 7760 | 4940 | 3890
|  |  | +105 Deg F |  | 10395 | 8635 | 7025 | 4405 | 3445
|  |  | +110 Deg F |  | 9460 | 7800 | 6290 | 3870 | 3000
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS18K6E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 73 | 228 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.2 | 33 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H325E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 16050 | 13740 | 11600 | 7610 | 5670
|  |  | +95 Deg F |  | 14770 | 12570 | 10530 | 6720 | 4870
|  |  | +100 Deg F |  | 13510 | 11410 | 9460 | 5840 | 4080
|  |  | +105 Deg F |  | 12280 | 10280 | 8420 | 4975 | 3295
|  |  | +110 Deg F |  | 11050 | 9150 | 7380 | 4110 | 2510
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS20K6E |  | 3 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11 Lb's | 5/8" | 1-1/8" | 73 | 246 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 16.7 | 96 | 3.1 | 12 | 30 | N/A | N/A | 38.5 | 50
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H325E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 16050 | 13740 | 11600 | 7610 | 5670
|  |  | +95 Deg F |  | 14770 | 12570 | 10530 | 6720 | 4870
|  |  | +100 Deg F |  | 13510 | 11410 | 9460 | 5840 | 4080
|  |  | +105 Deg F |  | 12280 | 10280 | 8420 | 4975 | 3295
|  |  | +110 Deg F |  | 11050 | 9150 | 7380 | 4110 | 2510
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS20K6E |  | 3 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11 Lb's | 5/8" | 1-1/8" | 73 | 246 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 10.2 | 75 | 3.1 | 12 | 25 | N/A | N/A | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H325E44-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F
|  |  | +90 Deg F |  | 16050 | 13740 | 11600 | 7610 | 5670
|  |  | +95 Deg F |  | 14770 | 12570 | 10530 | 6720 | 4870
|  |  | +100 Deg F |  | 13510 | 11410 | 9460 | 5840 | 4080
|  |  | +105 Deg F |  | 12280 | 10280 | 8420 | 4975 | 3295
|  |  | +110 Deg F |  | 11050 | 9150 | 7380 | 4110 | 2510
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS20K6E |  | 3 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11 Lb's | 5/8" | 1-1/8" | 73 | 246 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.6 | 40 | 2.5 | 6 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H100L44-DA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 6450 | 5490 | 4640 | 3880 | 3170 | 2500 | 1850
|  | +95 Deg F |  | 5920 | 5000 | 4210 | 3490 | 2830 | 2200 | 1580
|  | +100 Deg F |  | 5360 | 4500 | 3770 | 3100 | 2480 | 1900 | 1320
|  | +105 Deg F |  | 4960 | 4160 | 3450 | 2830 | 2250 | 1700 | 1170
|  | +110 Deg F |  | 4240 | 3500 | 2880 | 2320 | 1810 | 1320 | 850
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF04K6E |  | 1 | 1 | 5.9 Lb's | 11 Lb's | 3.3 Lb's | 8.6 Lb's | 3/8" | 5/8" | 74 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 8.6 | 59.2 | 0.5 | 4 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H100L44-EA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 6450 | 5490 | 4640 | 3880 | 3170 | 2500 | 1850
|  | +95 Deg F |  | 5920 | 5000 | 4210 | 3490 | 2830 | 2200 | 1580
|  | +100 Deg F |  | 5360 | 4500 | 3770 | 3100 | 2480 | 1900 | 1320
|  | +105 Deg F |  | 4960 | 4160 | 3450 | 2830 | 2250 | 1700 | 1170
|  | +110 Deg F |  | 4240 | 3500 | 2880 | 2320 | 1810 | 1320 | 850
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF04K6E |  | 1 | 1 | 5.9 Lb's | 11 Lb's | 3.3 Lb's | 8.6 Lb's | 3/8" | 5/8" | 74 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 5.7 | 52 | 0.5 | 4 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H100L44-GA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 6450 | 5490 | 4640 | 3880 | 3170 | 2500 | 1850
|  | +95 Deg F |  | 5920 | 5000 | 4210 | 3490 | 2830 | 2200 | 1580
|  | +100 Deg F |  | 5360 | 4500 | 3770 | 3100 | 2480 | 1900 | 1320
|  | +105 Deg F |  | 4960 | 4160 | 3450 | 2830 | 2250 | 1700 | 1170
|  | +110 Deg F |  | 4240 | 3500 | 2880 | 2320 | 1810 | 1320 | 850
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF04K6E |  | 1 | 1 | 5.9 Lb's | 11 Lb's | 3.3 Lb's | 8.6 Lb's | 3/8" | 5/8" | 74 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 2.9 | 26 | 0.4 | 2 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H150L44-DA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 10120 | 8920 | 7750 | 6600 | 5480 | 4440 | 3480
|  | +95 Deg F |  | 9470 | 8320 | 7200 | 6090 | 5030 | 4030 | 3130
|  | +100 Deg F |  | 8820 | 7710 | 6650 | 5600 | 4580 | 3640 | 2790
|  | +105 Deg F |  | 8160 | 7120 | 6100 | 5110 | 4150 | 3270 | 2470
|  | +110 Deg F |  | 7510 | 6520 | 5570 | 4630 | 3730 | 2900 | 2160
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF06K6E |  | 1.5 | 1 | 5.9 Lb's | 11 Lb's | 3.3 Lb's | 8.6 Lb's | 3/8" | 5/8" | 74 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 10.3 | 59.2 | 0.5 | 4 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H150L44-EA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 10120 | 8920 | 7750 | 6600 | 5480 | 4440 | 3480
|  | +95 Deg F |  | 9470 | 8320 | 7200 | 6090 | 5030 | 4030 | 3130
|  | +100 Deg F |  | 8820 | 7710 | 6650 | 5600 | 4580 | 3640 | 2790
|  | +105 Deg F |  | 8160 | 7120 | 6100 | 5110 | 4150 | 3270 | 2470
|  | +110 Deg F |  | 7510 | 6520 | 5570 | 4630 | 3730 | 2900 | 2160
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF06K6E |  | 1.5 | 1 | 5.9 Lb's | 11 Lb's | 3.3 Lb's | 8.6 Lb's | 3/8" | 5/8" | 74 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 6.3 | 52 | 0.5 | 4 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H150L44-GA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 10120 | 8920 | 7750 | 6600 | 5480 | 4440 | 3480
|  | +95 Deg F |  | 9470 | 8320 | 7200 | 6090 | 5030 | 4030 | 3130
|  | +100 Deg F |  | 8820 | 7710 | 6650 | 5600 | 4580 | 3640 | 2790
|  | +105 Deg F |  | 8160 | 7120 | 6100 | 5110 | 4150 | 3270 | 2470
|  | +110 Deg F |  | 7510 | 6520 | 5570 | 4630 | 3730 | 2900 | 2160
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF06K6E |  | 1.5 | 1 | 5.9 Lb's | 11 Lb's | 3.3 Lb's | 8.6 Lb's | 3/8" | 5/8" | 74 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.3 | 25.4 | 0.4 | 2 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H200L44-DA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 15650 | 13810 | 11990 | 10250 | 8580 | 7000 | 5530
|  | +95 Deg F |  | 14690 | 12910 | 11180 | 9510 | 7920 | 6420 | 5030
|  | +100 Deg F |  | 13740 | 12030 | 10380 | 8790 | 7280 | 5860 | 4540
|  | +105 Deg F |  | 12810 | 11150 | 9580 | 8080 | 6650 | 5300 | 4070
|  | +110 Deg F |  | 11850 | 10300 | 8810 | 7370 | 6020 | 4760 | 3610
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF09K6E |  | 2 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 3/8" | 7/8" | 75 | 219 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 15 | 87 | 1 | 6 | 25 | N/A | N/A | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H200L44-EA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 15650 | 13810 | 11990 | 10250 | 8580 | 7000 | 5530
|  | +95 Deg F |  | 14690 | 12910 | 11180 | 9510 | 7920 | 6420 | 5030
|  | +100 Deg F |  | 13740 | 12030 | 10380 | 8790 | 7280 | 5860 | 4540
|  | +105 Deg F |  | 12810 | 11150 | 9580 | 8080 | 6650 | 5300 | 4070
|  | +110 Deg F |  | 11850 | 10300 | 8810 | 7370 | 6020 | 4760 | 3610
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF09K6E |  | 2 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 3/8" | 7/8" | 75 | 219 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 9.2 | 72.2 | 1 | 6 | 15 | N/A | N/A | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H200L44-GA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 15650 | 13810 | 11990 | 10250 | 8580 | 7000 | 5530
|  | +95 Deg F |  | 14690 | 12910 | 11180 | 9510 | 7920 | 6420 | 5030
|  | +100 Deg F |  | 13740 | 12030 | 10380 | 8790 | 7280 | 5860 | 4540
|  | +105 Deg F |  | 12810 | 11150 | 9580 | 8080 | 6650 | 5300 | 4070
|  | +110 Deg F |  | 11850 | 10300 | 8810 | 7370 | 6020 | 4760 | 3610
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF09K6E |  | 2 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.9 Lb's | 3/8" | 7/8" | 75 | 219 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.9 | 35.8 | 0.8 | 3 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H300L44-DA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 20270 | 18020 | 15830 | 13690 | 11620 | 9600 | 7630
|  | +95 Deg F |  | 19040 | 16890 | 14800 | 12760 | 10780 | 8840 | 6950
|  | +100 Deg F |  | 17810 | 15770 | 13790 | 11840 | 9950 | 8100 | 6280
|  | +105 Deg F |  | 16590 | 14660 | 12780 | 10940 | 9130 | 7370 | 5630
|  | +110 Deg F |  | 15390 | 13560 | 11780 | 10040 | 8330 | 6660 | 5010
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF12K6E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.4 Lb's | 7.83 Lb's | 3/8" | 7/8" | 77 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 18.4 | 105 | 1 | 10 | 25 | N/A | N/A | 35 | 50
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H300L44-EA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 20270 | 18020 | 15830 | 13690 | 11620 | 9600 | 7630
|  | +95 Deg F |  | 19040 | 16890 | 14800 | 12760 | 10780 | 8840 | 6950
|  | +100 Deg F |  | 17810 | 15770 | 13790 | 11840 | 9950 | 8100 | 6280
|  | +105 Deg F |  | 16590 | 14660 | 12780 | 10940 | 9130 | 7370 | 5630
|  | +110 Deg F |  | 15390 | 13560 | 11780 | 10040 | 8330 | 6660 | 5010
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF12K6E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.4 Lb's | 7.83 Lb's | 3/8" | 7/8" | 77 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 11 | 85 | 1 | 10 | 25 | N/A | N/A | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A

## K_H300L44-GA_R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | K Series - Model KBH / KFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://kramer.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 10:48
|  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  | Ambient |  | Saturated Suction Temperature (SST)
|  | Temperature |  | 0 F | -5 F | -10 F | -15 F | -20 F | -25 F | -30 F
|  | +90 Deg F |  | 20270 | 18020 | 15830 | 13690 | 11620 | 9600 | 7630
|  | +95 Deg F |  | 19040 | 16890 | 14800 | 12760 | 10780 | 8840 | 6950
|  | +100 Deg F |  | 17810 | 15770 | 13790 | 11840 | 9950 | 8100 | 6280
|  | +105 Deg F |  | 16590 | 14660 | 12780 | 10940 | 9130 | 7370 | 5630
|  | +110 Deg F |  | 15390 | 13560 | 11780 | 10040 | 8330 | 6660 | 5010
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CF12K6E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.4 Lb's | 7.83 Lb's | 3/8" | 7/8" | 77 | 230 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 5.9 | 42 | 0.8 | 5 | 15 | N/A | N/A | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model KFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
K_SBMTL_1115-A